## Cover Page
v4.4
Notificaton/Application to DNO of installation of dedicated Electric Vehicle charging equipment (including V2G) and/or Heat Pump
Completing this form accurately will help DNOs process your application as quickly as possible. Please read the following information thoroughly before starting to ensure you have all information required to complete the relevant sections.
What is eligible
This spreadsheet is for Electric Vehicle Charge Points (EVCPs) or Heat Pumps (HPs) being installed in a premises with an existing Distribution Network Operator (DNO) connection electricity supply. This form may also be used for the installation of Vehicle-to-Grid Electric Vehicle Charge Points (V2G EVCPs) where the total aggregated capacity of generation/battery storage equipment in a premises is 3.68kW (single phase) or 11.04kW (3-phase) or less. To apply for a new connection to the network, please contact your relevant DNO.
When to complete
This form should always be reviewed prior to installing any new EVCP or HP to determine whether the installation requires an application or whether it is eligible for the notification process.
When to submit
If the installation meets all the notification criteria (see below) the DNO must be notified within 28 days of installing the new equipment. If all the notiffication criteria below cannot be met, you should submit an application to the DNO using this form before connecting the new equipment to ensure that the DNO can maintain safe and effective operation of the electricity network.
What to submit
Depending on the nature of the new equipment, the DNO may require additional information. For a single EVCP installation or HP installation or simultaneous installation of one EVCP & one HP in one premises, please complete the Single Electric Vehicles and Heat Pumps Installation Application Form, found on the ENA website: https://www.energynetworks.org/operating-the-networks/connecting-to-the-networks
For multiple pieces of equipment (including multiple pieces of equipment under one controller) or multiple premises, please complete this multiple installation spreadsheet (form found on second tab), also available on the ENA website at the link above.
For help identifying the correct DNO and their contact details please visit the ENA website: https://www.energynetworks.org/operating-the-networks/whos-my-network-operator
Any reinforcement costs associated with this installation may be recharged to the customer.
Required Information
To populate this form, you will need information about the following.
Device to be installed
Details of EVCPs or HPs to be installed are required. Where equipment is not registered in the relevant ENA database, additional information will be required (Section E). A link to the Heat Pump Database can be found on the Databases page (https://www.energynetworks.org/industry-hub/databases) on the ENA website: https://www.energynetworks.org/operating-the-networks/connecting-to-the-networks. Type tested V2G EVCPs can be found in the ENA Type Test Verification Report Register: https://www.ena-eng.org/gen-ttr/.
Existing devices at the premises
Details of any existing EVCPs, electric heating, battery storage, generation (e.g. solar PV), storage or other large load drawing devices.
Maximum Demand (MD)
A load survey is required to calculate the Maximum Demand. This should comprise the existing Maximum Demand of the whole premises and the new equipment to be installed as well as any import or load limiting devices. Further Guidance on such devices is available in the FAQ section of the Connecting to the networks page on the ENA website: https://www.energynetworks.org/operating-the-networks/connecting-to-the-networks
Supply Capacity / cut-out rating
If the cut-out rating cannot be established the ‘Apply to Connect’ process must be followed and the relevant timeframes are applicable.
If the cut-out rating is unknown, a photograph can be provided to the DNO. Please note that you MUST NOT open the cut-out. Further Guidance on cut-out ratings is available on the ENA website: https://www.energynetworks.org/operating-the-networks/connecting-to-the-networks
Adequacy of supply
An ‘adequacy of supply’ assessment is required prior to installing a EVCP or HP. The DNO must be contacted in advance of installation where there is an identified issue with adequacy or a safety concern with the premises existing DNO service equipment.
Timescales
Providing that this form is fully and correctly completed, the following timeframes are applicable:
Notifications
Provided the installation meets all the relevant notification criteria (i.e. all the applicable checkboxes in Section B that are relevant to the installation can be ticked) installers can connect the new EVCP of HP and notify the DNO using this form within 28 days of their installation.
Application (60A < MD ≤ 100A)
The DNO will assess the supply capacity and confirm if the new equipment can be connected within 10 working days of receiving the completed form.
Application (MD > 100A)
Timescales as per the Northern Ireland Electricity - Electricity Distribution Licence: https://www.nienetworks.co.uk/documents/regulatory-documents/nie-distribution-licence-effective-22-january-2018.aspx.
Notification Criteria
  All Equipment types
  - Only connecting one additional piece of equipment (EV Charge Point or Heat Pump)
  - DNO cut-out rating known
  - No safety concerns over adequacy of DNO service equipment
  - No other issues identified with adequacy or integrity of DNO service equipment
  - Not identified as a Looped Service
  - Metered supply
  - Maximum Demand less than the known cut-out rating
  - Maximum Demand less than 13.8kVA per phase OR the premises is CT metered OR the premises load is limited to below the known cut-out fuse rating
  HP only
  - Heat pump system under single controller only
  - Total heat pump system Maximum Demand ≤32A
  - Model marked at ‘Connect and Notify’ in the ENA’s HP Database
  EVCP only
  - AC Output
  - Premises MD ≤13.8 kVA per phase OR where CT metered: Maximum AC output of EV charge points ≤30% of the Maximum Import Capacity
  V2G only
  - Total installed generating capacity (including any PV, storage or V2G storage) ≤3.68kW (16A) per phase and excluding any export limiting device
  - V2G EVCP charge point Fully Type Tested and registered in the ENA Type Test Verification Report Register
Does the installation meet all notification criteria above? (If yes, input the date of installation into the "SECTION B: Notification Criteria" column on the Form tab of this document. If no, leave this column blank).
NO - Apply to the DNO before installation
YES - If yes, i.e., all applicable notification criteria above are met, you can connect the equipment and notify the DNO within 28 days

## Form
SECTION A: Installer Contact | [7 empty] | SECTION A: Customer Details | [7 empty] | SECTION B: Notification Criteria | SECTION C: Electricity Supply Details | [18 empty] | SECTION D: Existing equipment at premises if applicable (this section is for V2G EVCP applications only) | [10 empty] | SECTION E: Details of device to be Installed |  |  | SECTION E: EVCP Details |  |  |  | SECTION E: V2G EVCP Details |  |  |  |  | SECTION E: HP Details | [5 empty] | SECTION F: Please fill in the following additional Power Quality details required for non-registered Heat Pump Models | [5 empty] | Further Comments
Name | Company | Installer Address Line 1 | Installer Address Line 2 | Town | Postcode | Phone | Email | Customer Name | Installation Address Line 1 | Installation Address Line 2 | Town | Postcode | Contact | Email | If necessary, are we able to contact the customer directly e.g. to arrange a fuse upgrade (YES/NO) | If all notification Criteria relevant to the equipment being installed is met, state the date of installation (DD/MM/YYYY) | Type of premises | MPRN (11 Digits) | DNO | Smart meter installed | Declared Voltage at Connection Point (Volts) | Number of phases | Max. Demand of Premises inc. load management, if applicable (Amps - Whole Current Metered, or kVA - CT Metered) | Supply Capacity (Amps or kVA) | Max. Demand all EVCPs/HPs combined can draw (Amps) | Has the DNO been contacted about this installation | Premises Cut-out rating - If known. Whole Current Metered only (Amps) | Import or load limiting device on premises | If yes, please confirm MD of the premises with load limiting device installed: | G100 export limiting scheme on premises | If yes, please detail | Any issues identified with the existing supply equipment? | If yes, please detail | Final or Proposed Earthing Arrangements | Looped Service? | Are there any existing LCT pieces of equipment installed at the premise? | Technology Type | If "Other" Technology Type, please specify | Approximate date of installation | Manufacturer | Manufacturer's reference number (where available) | Registered Capacity (kW) |  | Phase (if known) | Power Factor | Device to be removed | Type of Equipment | Phase | Maximum Current Demand of proposed equipment | EVCP Manufacturer | EVCP Model | Is the model listed on the EVCP Database (DC only)? | If yes, please reference the Product ID | V2G EVCP Manufacturer | V2G EVCP Model | Export Capacity of V2G EVCP (kW) | Is the model listed on the ENA Type Test Verification Report Register? | If yes, please reference the Product ID | HP Manufacturer | HP Model | Heating Only HP or Heating and Cooling? (if applicalbe) | Does the HP have additional components installed? | If yes, please detail | ENA Heat Pump Database Register Number - If Applicable | For non-registered HP models, is the Heat Pump Datasheet and Power Quality Documentation attached to this application? | Does the HP installation meet the Microgeneration Certificate Scheme Product Requirements? | Harmonics: Does the proposed HP installation comply with the technical requirements of BS EN/IEC 61000-3-2? | Harmonics: Does the proposed HP installation comply with BS EN/IEC 61000-3-12? | Flicker: Does the proposed HP installation comply with the technical requirements of BS EN/IEC 61000-3-3? | Flicker: Does the proposed HP installation comply with BS EN/IEC 61000-3-11?
[42 empty] | Import | Export
John Smith | Example Renewables | 3 Elsmere Way |  | Rickmansworth | WD4 5BG | 020 7706 5164 | john.smith@examplerenewables.com | Joe Bloggs | 1 Example Road | Westminster | London | SW1P 2AF |  | joe.bloggs@gmail.com |  | 2021-07-24 | Residential house | 81234567890 | NIE Networks | Yes | 230 | Single Phase | 52A | 100A | 32 | Yes | 1 | No |  | Yes | Text | No |  | TN-S (SNE) | No | Yes | Solar PV | [9 empty] | Heat Pump | [11 empty] | Panasonic | WH-MXC12G6E5 | Heating and cooling | Yes |  | HP_0701 | N/a | Yes | N/a | Yes (Rsce = 33) | N/a | Yes (meets 61000-3-3 tech. requirements) | N/a | EV Charge Point | 1*16A | Single Phase | TN-C-S (PME) | Yes | Heating only | Back-up heater - on-board | Single Phase | Yes (Rsce = 33) | Yes (meets 61000-3-3 tech. requirements)
John Smith | Example Renewables | 3 Elsmere Way |  | Rickmansworth | WD4 5BG | 020 7706 5164 | john.smith@examplerenewables.com | Sheila Flanagan | 39 Rivendale Road | Aldershot | Surrey | GU12 9AJ |  | Sheila.flanagan@hotmail.co.uk |  |  | Residential flat | 80987654321 | NIE Networks | No | 230 | Three Phase | 42A | 100A | 32 | Yes | N/a | No |  | Yes |  | No |  | TT (Direct) | No | No | [10 empty] | EVCP | [17 empty] | N/a | Yes | N/a | Yes (Rsce = 33) | N/a |  | N/a | Heat Pump | 2*16A | Split/two Phase | TN-S (SNE) | No | Heating and cooling | Back-up heater - external | Three Phase | Yes, subject to minimum short-circuit power (Ssc) | Yes, subject to a service current capacity ≥100A per phase
[73 empty] | 1*32A & 1*16A |  | Customer Substation (HV CT metered) |  |  | Supplementary (boost) heater - external |  |  | No
[73 empty] | 2*32A |  |  |  |  | Water (immersion) heater - on-board
[73 empty] | 2*32A & 1*16A |  |  |  |  | Water (immersion) heater - external
[73 empty] | 2*32A & 2*16A |  |  |  |  | N/a
1*64A
1*128A
N/a
Note on BH1: This section (columns AR through BB) does not need to be completed for EV charge point installations
Note on BN1: This section does not need to be completed if the HP is in the ENA HP Database and you have confirmed that the information in the database is correct and accurate
Note on Q2: Notification criteria can be found on the 'cover page' tab of this form. If the equipment to be installed does not meet all relevant notifcation criteria, please apply to the DNO before connecting the equipment and leave this field blank
Note on AI2: Detail the final earthing arrangements that have been applied for the installation of the charging point as per BS 7671 and IET Code of Practice e.g. protective multiple earthing (PME).
Note on AL2: If there are more than one existing LCT pieces of equipment in one premises, please merge rows within Section A - C and Sections E - F as appropriate.
Note on BA2: If Yes - please complete column BB. If No then you MUST attach Datasheet and Power Quality documentation for the EVCP (Rated power, harmonic emission data & test standard applied for harmonic emission data)
Note on BF2: If Yes, please complete Column BE. If No, Form A2-1 or A2-2 or A2-3 (as appropriate) should be submitted to the DNO with this form. These forms can be downloaded from the ENA website Resource Library: https://www.energynetworks.org/industry-hub/resource-library/
Note on BK2: If the Heat Pump has multiple additional components, please copy this column and add additional columns accordingly.
Note on BM2: This is in the database found in the second paragraph under “Processes & Forms” on the ENA website. If the Heat Pump model is not in the ENA Heat Pump Database then please attach the datasheet(s) and other power quality documentation(s) when sending this spreadsheet, as well as filling out the following section (columns BL through BQ)
Note on BN2: Must be provided
Note on BO2: https://www.microgenerationcertification.org/mcs-standards/product-standards/heat-pumps/

## Validation (hidden)
Type of premises | Smart Meter | Number of phases | Supply capacity confirmed by DNO | Import or load limiting devices on premises | G100 export limiting scheme on premises | Any issues identified with existing supply equipment | Final or proposed earthing arrangements | Service looped | Technology Type | Device to be removed | Existing device | EV CP listed | HP Operating Mode | Heating elements required? | Heating Elements
Residential house | Yes | Single Phase | Yes | Yes | Yes | Yes | TN-C-S (PME) | Yes, multiple service cables present | Heat Pump | Yes | Yes | Yes | Heating & Cooling | Yes | Back-up heater - On-board
Residential flat | No | Split/two Phase | No | No | No | No | TN-S (SNE) | No | EVCP | No | No | No | Heating only | No | Back-up heater - External
Commercial |  | Three Phase |  |  |  |  | TT (Direct) |  | V2G EVCP | [5 empty] | Boost heater - On-board
Public | [6 empty] | Customer Substation (HV CT metered) |  | Solar PV | [5 empty] | Boost heater - External
Other | [8 empty] | Battery Storage | [5 empty] | Immersion heater - On-board
[9 empty] | Other | [5 empty] | Immersion heater - External